## Baseline
HE Carbon Management - Rapid assessment of potential (RAP)
Produced by Carbon Insight
Issue Log
2009-07-06 | Generic Version Based on LACM Version 2.2
2009-07-08 | Based on Generic Version 1.2
2009-07-08 | HE CM RAP tool V1.0
2009-07-09 | V1.1 modification of benchmark referencing to allow for inserting of new benchmarks
KEY:
Name of Higher Education Organisation |  |  |  | Light blue cells are for data input
Yellow cells are automatically calculated but can be overwritten with actual data
Table 1 Buildings
| Category | Building Type | Floor area (m2) | Fossil fuel demand (kWh/yr) | Electricity demand (kWh/yr) | Baseline emissions (tCO2/yr) | Annual energy bill (£/yr)
| halls | Office - AirCon Prestige type4 | 36666 | 6264386.1 | 11157463.8 | 7150.5047 | 1080528.687
| Buildings Category 2 | Lecture room, arts | 100000 | 12000000 | 7600000 | 6300.992 | 968000
| Buildings Category 3 | Library, air conditioned | 8000 | 1960000 | 3232000 | 2098.1898 | 317360
| Buildings Category 4 |  |  | 0 | 0 | 0 | 0
| Buildings Category 5 |  |  | 0 | 0 | 0 | 0
| Buildings Category 6 |  |  | 0 | 0 | 0 | 0
| Buildings Category 7 |  |  | 0 | 0 | 0 | 0
| Totals |  | 144666 | 20224386.1 | 21989463.8 | 15549.6865 | 2365888.687
| Not Accounted for |  |  | 0 | 0 | 0 | 0
Import from Baseline tool
Table 2 Buildings
| Category | Total Fossil kWh | Total Elec kWh
Buildings Category 1
Buildings Category 2
Buildings Category 3
Buildings Category 4
Buildings Category 5
Buildings Category 6
Buildings Category 7
Not Accounted for
Table 3 Transport kg CO2
| Category | Petrol | Diesel | Air | Total | Annual fuel bill (£/yr)
| Transport Category 1 |  |  |  | 0 | 0
| business Air |  |  |  | 0 | 0
| Transport Category 3 |  |  |  | 0 | 0
| Transport Category 4 |  |  |  | 0 | 0
| Transport Category 5 |  |  |  | 0 | 0
| Transport Category 6 |  |  |  | 0 | 0
| Transport Category 7 |  |  |  | 0 | 0
| Not Accounted for |  |  |  | 0 | 0
| Total Accounted for | 0 | 0 | 0 | 0 | 0
This tool has been designed by Carbon Insight to help clients rapidly review potential for carbon savings across their building portfolio.
Copy and paste the data from the baseline tool into the tables 2 and 3 below.
If baseline data is unavailable , approximate consumptions figures can be obtained by inputting floor areas with the corresponding building type into table 1.
Please note if air travel is being considered it will need to have a separate transport category in this tool. This will mean air travel will need to have a separate category in the baseline tool. In addition, financial costs and savings associated with air travel are not calculated in this version of the tool.
Note on F22: If data has not been imported from baseline, floor are is multiplied by DEC benchmarks
Note on G22: If data has not been imported from baseline, floor are is multiplied by DEC benchmarks
Note on H22: Carbon emissions assume standard grid electricity and all heating from gas
Note on F54: Air Travel must be in a separate category to Petrol or Diesel
Note on H54: Currently excludes costs relating to Air Travel

## Opportunities
Opportunities for carbon reduction
EASE
[18 empty] | 1 | 2 | 3
[17 empty] | Effect | 4 | 5 | 6
[18 empty] | 7 | 8 | 9
|  | halls | Buildings Category 2 | Buildings Category 3 | Buildings Category 4 | Buildings Category 5 | Buildings Category 6 | Buildings Category 7
|  | Transport Category 1 | business Air | Transport Category 3 | Transport Category 4 | Transport Category 5 | Transport Category 6 | Transport Category 7 | Renewable energy
Buildings Category 1
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Annual gas saving (kWh) | Annual elec saving (KWh) | Annual carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for follow up (Y/N) | Ease and effect score (1-9)
|  | halls | Air conditioning | Free cooling | 0% | 0% | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
1 |  | halls | Heating - controls | Heating control systems | 100% | 30% | 93.94% | 15% |  | 641 |  | 264812.6851 | 0 | 48.9824 | 31397.7199 | 7944.3806 | 3.9522 | 0.315% | YES | 4 | Buildings
2 |  | halls | Heating - controls | Optimum start controls | 100% | 30% | 93.94% | 10% |  | 396 |  | 176541.7901 | 0 | 32.6549 | 12931.3542 | 5296.2537 | 2.4416 | 0.21% | YES |  | Buildings
3 |  | halls | Heating - controls | Sequencing | 100% | 30% | 93.94% | 7% |  | 470 |  | 123579.2531 | 0 | 22.8585 | 10743.4736 | 3707.3776 | 2.8979 | 0.147% | YES |  | Buildings
4 |  | halls | Heating - controls | Zoning | 100% | 30% | 93.94% | 5% |  | 682 |  | 88270.895 | 0 | 16.3275 | 11135.3328 | 2648.1269 | 4.205 | 0.105% | YES |  | Buildings
5 |  | halls | Heating - pipework insulation | Pipework insulation | 100% | 30% | 5% | 70% |  | 472 |  | 65776.054 | 0 | 12.1666 | 5742.6337 | 1973.2816 | 2.9102 | 0.07824% | YES |  | Buildings
6 |  | halls | Heating - replacement boilers | Fuel switching to biofuel | 100% | 30% | 100% | 80% |  | 803 |  | 1503452.664 | 0 | 278.0936 | 223309.1923 | 45103.5799 | 4.951 | 1.788% | YES |  | Buildings
7 |  | halls | Heating - replacement boilers | Upgrade to condensing boilers | 100% | 30% | 100% | 20% |  | 803 |  | 375863.166 | 0 | 69.5234 | 55827.2981 | 11275.895 | 4.951 | 0.4471% | YES |  | Buildings
8 |  | halls | ICT | IT Management software | 100% | 30% | 17.65% |  | 10% | 294 |  | 0 | 59068.926 | 31.7212 | 9326.0312 | 4725.5141 | 1.9735 | 0.204% | YES |  | Buildings
9 |  | halls | ICT | LCD flat screens | 100% | 30% | 17.65% |  | 10% | 4202 |  | 0 | 59068.926 | 31.7212 | 133292.4599 | 4725.5141 | 28.207 | 0.204% | YES |  | Buildings
10 |  | halls | ICT | Printer rationalisation | 100% | 30% | 17.65% |  | 10% | 1200 |  | 0 | 59068.926 | 31.7212 | 38065.4336 | 4725.5141 | 8.0553 | 0.204% | YES |  | Buildings
11 |  | halls | ICT | Virtualisation/thin computers | 100% | 30% | 2.941% |  | 50% | 606 |  | 0 | 49224.105 | 26.4343 | 16019.2033 | 3937.9284 | 4.0679 | 0.17% | YES |  | Buildings
12 |  | halls | Lighting - controls | Automatic lighting controls | 100% | 30% | 50% |  | 35% | 1200 |  | 0 | 585766.8495 | 314.5685 | 377482.2162 | 46861.348 | 8.0553 | 2.023% | YES |  | Buildings
13 |  | halls | Lighting - controls | Localised lighting | 100% | 30% | 50% |  | 50% | 500 |  | 0 | 836809.785 | 449.3836 | 224691.7954 | 66944.7828 | 3.3564 | 2.89% | YES |  | Buildings
14 |  | halls | Lighting - replacement fittings | Retrofit/replace lighting to T5 | 100% | 30% | 50% |  | 8% | 633 |  | 0 | 133889.5656 | 71.9014 | 45513.5701 | 10711.1652 | 4.2492 | 0.4624% | YES |  | Buildings
15 |  | halls | Misc | Awareness raising campaign | 100% | 30% | 100% | 7% | 7% | 500 |  | 131552.1081 | 234306.7398 | 150.1606 | 75080.2994 | 22691.1024 | 3.3088 | 0.9657% | YES |  | Buildings
16 |  | halls | Misc | Equipment timer controls | 100% | 30% | 5.882% |  | 40% | 307 |  | 0 | 78758.568 | 42.2949 | 12984.5423 | 6300.6854 | 2.0608 | 0.272% | YES |  | Buildings
|  | halls | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | halls | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 2729848.6155 | 2095962.3909 | 1630.5138
[10 empty] | Savings as a % of halls emissions |  | 43.58% | 18.79% | 22.8%
Buildings Category 2
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 2 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
17 |  | Buildings Category 2 | BMS fine tuning | BMS fine tuning | 100% | 30% | 50% | 5% | 2% | 470 |  | 90000 | 22800 | 28.8914 | 13578.9373 | 4524 | 3.0015 | 0.1858% | YES |  | Buildings
|  | Buildings Category 2 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
18 |  | Buildings Category 2 | Building fabric | Loft insulation | 100% | 30% | 93.94% | 5% |  | 566 |  | 169090.9091 | 0 | 31.2767 | 17702.6379 | 5072.7273 | 3.4898 | 0.2011% | YES |  | Buildings
|  | Buildings Category 2 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
19 |  | Buildings Category 2 | Heating - controls | Heating control systems | 100% | 30% | 93.94% | 15% |  | 641 |  | 507272.7273 | 0 | 93.8302 | 60145.1815 | 15218.1818 | 3.9522 | 0.6034% | YES |  | Buildings
|  | Buildings Category 2 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
20 |  | Buildings Category 2 | Heating - controls | Sequencing | 100% | 30% | 93.94% | 7% |  | 470 |  | 236727.2727 | 0 | 43.7874 | 20580.0985 | 7101.8182 | 2.8979 | 0.2816% | YES |  | Buildings
|  | Buildings Category 2 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
21 |  | Buildings Category 2 | Lighting - controls | Automatic lighting controls | 50% | 30% | 50% |  | 35% | 1200 |  | 0 | 199500 | 107.1355 | 128562.588 | 15960 | 8.0553 | 0.689% | YES |  | Buildings
|  | Buildings Category 2 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 2 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 1003090.9091 | 222300 | 304.9213
[10 empty] | Savings as a % of Buildings Category 2 emissions |  | 8.359% | 2.925% | 4.839%
Buildings Category 3
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 3 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - controls | Heating control systems |  |  | 93.94% | 15% |  | 641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - controls | Sequencing |  |  | 93.94% | 7% |  | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Lighting - controls | Automatic lighting controls |  |  | 50% |  | 35% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 3 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 0 | 0 | 0
[10 empty] | Savings as a % of Buildings Category 3 emissions |  | 0% | 0% | 0%
Buildings Category 4
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 4 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - controls | Heating control systems |  |  | 93.94% | 15% |  | 641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - controls | Sequencing |  |  | 93.94% | 7% |  | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Lighting - controls | Automatic lighting controls |  |  | 50% |  | 35% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 4 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 0 | 0 | 0
[10 empty] | Savings as a % of Buildings Category 4 emissions |  | #DIV/0! | #DIV/0! | #DIV/0!
Buildings Category 5
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 5 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - controls | Heating control systems |  |  | 93.94% | 15% |  | 641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - controls | Sequencing |  |  | 93.94% | 7% |  | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Lighting - controls | Automatic lighting controls |  |  | 50% |  | 35% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 5 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 0 | 0 | 0
[10 empty] | Savings as a % of Buildings Category 5 emissions |  | #DIV/0! | #DIV/0! | #DIV/0!
Buildings Category 6
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 6 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - controls | Heating control systems |  |  | 93.94% | 15% |  | 641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - controls | Sequencing |  |  | 93.94% | 7% |  | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Lighting - controls | Automatic lighting controls |  |  | 50% |  | 35% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 6 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 0 | 0 | 0
[10 empty] | Savings as a % of Buildings Category 6 emissions |  | #DIV/0! | #DIV/0! | #DIV/0!
Buildings Category 7
|  | Area | Technology category | Technology | % applicable | % opportunity | % of utility | % Gas saving | % Elec saving | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Buildings Category 7 | Air conditioning | Free cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Air conditioning server rooms | Optimise control of cooling |  |  | 2.941% |  | 5% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | BMS fine tuning | BMS fine tuning |  |  | 50% | 5% | 2% | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | BMS upgrades | BMS |  |  | 50% | 5% | 2% | 427 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Building fabric | Cavity wall insulation |  |  | 93.94% | 5% |  | 628 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Building fabric | Draught proofing |  |  | 93.94% | 10% |  | 574 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Building fabric | Loft insulation |  |  | 93.94% | 5% |  | 566 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Building fabric | Secondary glazing |  |  | 93.94% | 10% |  | 750 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - controls | Heating control systems |  |  | 93.94% | 15% |  | 641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - controls | Optimum start controls |  |  | 93.94% | 10% |  | 396 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - controls | Sequencing |  |  | 93.94% | 7% |  | 470 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - controls | Zoning |  |  | 93.94% | 5% |  | 682 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - pipework insulation | Pipework insulation |  |  | 5% | 70% |  | 472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - replacement boilers | Fuel switching to biofuel |  |  | 100% | 80% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Heating - replacement boilers | Upgrade to condensing boilers |  |  | 100% | 20% |  | 803 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | ICT | IT Management software |  |  | 17.65% |  | 10% | 294 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | ICT | LCD flat screens |  |  | 17.65% |  | 10% | 4202 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | ICT | Printer rationalisation |  |  | 17.65% |  | 10% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | ICT | Virtualisation/thin computers |  |  | 2.941% |  | 50% | 606 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Lighting - controls | Automatic lighting controls |  |  | 50% |  | 35% | 1200 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Lighting - controls | Localised lighting |  |  | 50% |  | 50% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Lighting - replacement fittings | Retrofit/replace lighting to T5 |  |  | 50% |  | 8% | 633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Awareness raising campaign |  |  | 100% | 7% | 7% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Equipment timer controls |  |  | 5.882% |  | 40% | 307 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Pool covers |  |  | 50% | 5% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Pool covers w/ vent fine tune |  |  | 100% | 10% | 15% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Swimming pool CHP |  |  | 100% |  | 40% | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Swimming pool heat recovery |  |  | 50% | 20% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Misc | Voltage optimisation |  |  | 100% |  | 10% | 503 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Ventilation - Variable speed drives | Variable speed drives |  |  | 15% |  | 35% | 458 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Steam Plant | Boiler TDS blowdown controls & boiler RO plant |  |  | 100% | 1% |  | 121 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Steam Plant | Install boiler economizers |  |  | 100% | 7% |  | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Steam Plant | Steam trap management |  |  | 100% | 2% |  | 153 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Buildings Category 7 | Other technologies | [6 empty] | 500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [8 empty] | Totals |  | 0 | 0 | 0
[10 empty] | Savings as a % of Buildings Category 7 emissions |  | #DIV/0! | #DIV/0! | #DIV/0!
Transport
Opportunities for carbon reduction
Transport Category 1
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
22 |  | Transport Category 1 |  | Effective travel plans | 50% | 100% | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES | 3
23 |  | Transport Category 1 |  | Low carbon replacement vehicles | 50% | 100% | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES
24 |  | Transport Category 1 |  | Biodiesel replacement fuel | 50% | 100% |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES
25 |  | Transport Category 1 |  | Fuel management | 50% | 100% | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES
26 |  | Transport Category 1 |  | Driver training & maintenance | 50% | 100% | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES
|  | Transport Category 1 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 1 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 1 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 1 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 1 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 1 emissions | #DIV/0!
Transport Category 2
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | business Air |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
27 |  | business Air |  | Web Conference | 100% | 50% |  |  | 25% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | YES
|  | business Air |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | business Air |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of business Air emissions | #DIV/0!
Transport Category 3
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | Transport Category 3 |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transport Category 3 |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 3 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 3 emissions | #DIV/0!
Transport Category 4
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | Transport Category 4 |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transport Category 4 |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 4 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 4 emissions | #DIV/0!
Transport Category 5
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | Transport Category 5 |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transport Category 5 |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 5 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 5 emissions | #DIV/0!
Transport Category 6
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | Transport Category 6 |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transport Category 6 |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 6 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 6 emissions | #DIV/0!
Transport Category 7
|  | Area |  | Carbon saving opportunity | % applicable | % opportunity | % savings |  |  | £/tonne CO2 | Total Petrol Saving (kWh/yr) | Total Diesel Saving (kWh/yr) | Total Air Saving (kWh/yr) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
[7 empty] | Petrol | Diesel | Air
|  | Transport Category 7 |  | Effective travel plans |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transport Category 7 |  | Low carbon replacement vehicles |  |  | 50% | 50% | 50% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Biodiesel replacement fuel |  |  |  | 5% |  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Fuel management |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Driver training & maintenance |  |  | 10% | 10% | 10% | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
|  | Transport Category 7 |  | Other technologies | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
[13 empty] | Savings as a % of Transport Category 7 emissions | #DIV/0!
Opportunities for renewable energy
|  | Area | Amount | Technology | Metric used |  |  |  | Total carbon saving (tCO2) | £/tonne CO2 |  | Total gas saving (kWh) | Total elec saving (KWh) | Total carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Select for export (Y/N) | Ease and effect score (1-9)
|  | Renewables |  | Photovoltaics | Potential area of panels (m2) |  |  |  | 0 | 9000 |  |  | 0 | 0 | 0 | 0 | 0 | 0%
|  | Renewables |  | Biomass | see buildings sheet - fuel switching
|  | Renewables |  | Small wind (6kW turbines) | Potential number of turbines |  |  |  | 0 | 14000 |  |  | 0 | 0 | 0 | 0 | 0 | 0%
|  | Renewables |  | Large wind (2MW turbines) | Potential number of turbines |  |  |  | 0 | 1300 |  |  | 0 | 0 | 0 | 0 | 0 | 0%
|  | Renewables |  | Solar hot water | Potential number of domestic equivalent systems (4m2) |  |  |  | 0 | 3200 |  | 0 |  | 0 | 0 | 0 | 0 | 0%
| Back to top | [11 empty] | Totals | 0
For each group of sites we have listed opportunities for carbon reductions and the likely saving. The user should fill in the blue cells with the percentage of the baseline this opportunity might be 'applicable' to, then of this percentage the likely 'opportunity' for the carbon reduction to be implemented.
Note: Carbon reduction opportunities will overlap, for example insulating a building will reduce the potential saving from boiler replacement. Be cautious of this in estimates and if unsure contact you Technical Consultant.
Transport Costs of Implementation: An estimation has been used of £500/tCO2 for all costs associated with implementing transport related opportunities.
Note on H12: i.e. space heating is typically 94% of gas consumption
Note on H13: Working Estimate
Note on K13: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on H14: Working Estimate
Note on K14: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on H15: Working Estimate
Note on I15: from previous project
Note on J15: As 50% Utility is too high for electricity for BMS savings thid figure has been reeduced to 2%
Note on K15: Previous projects
Note on H16: Working Estimate
Note on I16: from previous project
Note on J16: As 50% Utility is too high for electricity for BMS savings thid figure has been reeduced to 2%
Note on K16: Ref: Salix
Note on I17: Mid range values from EPG312
Note on K17: Ref: Salix
Note on I18: Mid range values from EPG312
Note on K18: Ref: Salix
Note on I19: Mid range values from EPG312
Note on K19: Ref: Salix
Note on I20: Mid range values from EPG312
Note on K20: Ref: Salix
Note on I21: Mid range values from EPG312
Note on K21: Ref: Salix
Note on I22: Working estimate
Note on K22: Ref: Salix
Note on I23: Reference LACM Deck of Cards
Note on K23: Previous projects
Note on I24: Working estimate
Note on K24: Previous projects
Note on H25: Derived from ECG019
Note on I25: Mid range values from EPG312
Note on K25: Ref: Salix
Note on I26: Based on carbon saving from biomass boilers
Note on K26: Previous projects
Note on I27: Mid range values from EPG312
Note on K27: Previous projects
Note on J28: working estimate
Note on K28: Previous projects
Note on J29: working estimate
Note on K29: Previous projects
Note on J30: working estimate
Note on K30: Previous projects
Note on H31: Working estimate
Note on J31: working estimate
Note on K31: Previous projects
Note on J32: Mid range values from EPG312
Note on K32: Previous projects
Note on J33: Mid range values from EPG312
Note on K33: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on J34: Mid range values from EPG312
Note on K34: Ref: Salix
Note on I35: Carbon Trust guide to awareness raising campaigns
Note on J35: Carbon Trust guide to awareness raising campaigns
Note on K35: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on J36: Mid range values from EPG312
Note on K36: Ref: Salix
Note on I37: Mid range values from EPG312
Note on K37: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on I38: Typical estimate
Note on J38: Typical estimate
Note on K38: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on J39: Mid range values from EPG312
Note on K39: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on H40: Based on pool heating
Note on I40: Mid range values from EPG312
Note on K40: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on H41: Derived from ECG019
Note on J41: Reference LACM Deck of Cards
Note on K41: Previous projects
Note on H42: Working Estimate
Note on J42: Mid range values from EPG312
Note on K42: Ref: Salix
Note on I43: from previous project
Note on K43: from previous project
Note on I44: from previous project
Note on I45: from previous project
Note on K45: from previous project
Note on K46: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on K47: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on K48: £500/tonne CO2 is Salix average for all projects. Used where better data is unavailable
Note on K443: Working estimate from typical project
Note on K445: Working estimate from typical project
Note on K446: Working estimate from typical project
Note on K447: Working estimate from typical project
Note on M447: Based on replacing gas fired hot water heater

## Selected opps
Selected opportunities
If you selected "YES" under 'Select for follow up' on the Opportunities tab, the project should be listed below.
These projects are estimated to produce a total carbon saving of |  |  |  |  | 1935.4351 | tonnes of CO2
The capital cost of these projects is estimated at |  |  |  |  | 1524111.9992
With an average payback period of |  |  |  |  | 5.1239 | years
This is equivalent to |  |  |  |  | 12.45% | of the estimated baseline
1
Ref | Area | Technology category | Technology | % applicable | % opportunity | Opportunity summary | Emissions source 1 | Amount saved emissions source 1 (kWh) | Emissions source 2 | Amount saved emissions source 2 (kWh) | Annual carbon saving (tCO2) | Capital cost | Annual cost saving | Simple payback (years) | % of total baseline | Ease and effect score (1-9)
Column # | 3 | 4 | 5 | 6 | 7 |  |  | 13 |  | 14 | 15 | 16 | 17 | 18 | 19 | 21
Totals row | [10 empty] | 1935.4351 | 1524111.9992 | 297449.177 | 5.1239 | 12.45%
1 | halls | Heating - controls | Heating control systems | 100% | 30% | Heating control systems could apply to 30% of our halls | Natural gas | 264812.6851 | Electricity (grid) | 0 | 48.9824 | 31397.7199 | 7944.3806 | 3.9522 | 0.315% | 4
2 | halls | Heating - controls | Optimum start controls | 100% | 30% | Optimum start controls could apply to 30% of our halls | Natural gas | 176541.7901 | Electricity (grid) | 0 | 32.6549 | 12931.3542 | 5296.2537 | 2.4416 | 0.21% | 0
3 | halls | Heating - controls | Sequencing | 100% | 30% | Sequencing could apply to 30% of our halls | Natural gas | 123579.2531 | Electricity (grid) | 0 | 22.8585 | 10743.4736 | 3707.3776 | 2.8979 | 0.147% | 0
4 | halls | Heating - controls | Zoning | 100% | 30% | Zoning could apply to 30% of our halls | Natural gas | 88270.895 | Electricity (grid) | 0 | 16.3275 | 11135.3328 | 2648.1269 | 4.205 | 0.105% | 0
5 | halls | Heating - pipework insulation | Pipework insulation | 100% | 30% | Pipework insulation could apply to 30% of our halls | Natural gas | 65776.054 | Electricity (grid) | 0 | 12.1666 | 5742.6337 | 1973.2816 | 2.9102 | 0.07824% | 0
6 | halls | Heating - replacement boilers | Fuel switching to biofuel | 100% | 30% | Fuel switching to biofuel could apply to 30% of our halls | Natural gas | 1503452.664 | Electricity (grid) | 0 | 278.0936 | 223309.1923 | 45103.5799 | 4.951 | 1.788% | 0
7 | halls | Heating - replacement boilers | Upgrade to condensing boilers | 100% | 30% | Upgrade to condensing boilers could apply to 30% of our halls | Natural gas | 375863.166 | Electricity (grid) | 0 | 69.5234 | 55827.2981 | 11275.895 | 4.951 | 0.4471% | 0
8 | halls | ICT | IT Management software | 100% | 30% | IT Management software could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 59068.926 | 31.7212 | 9326.0312 | 4725.5141 | 1.9735 | 0.204% | 0
9 | halls | ICT | LCD flat screens | 100% | 30% | LCD flat screens could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 59068.926 | 31.7212 | 133292.4599 | 4725.5141 | 28.207 | 0.204% | 0
10 | halls | ICT | Printer rationalisation | 100% | 30% | Printer rationalisation could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 59068.926 | 31.7212 | 38065.4336 | 4725.5141 | 8.0553 | 0.204% | 0
11 | halls | ICT | Virtualisation/thin computers | 100% | 30% | Virtualisation/thin computers could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 49224.105 | 26.4343 | 16019.2033 | 3937.9284 | 4.0679 | 0.17% | 0
12 | halls | Lighting - controls | Automatic lighting controls | 100% | 30% | Automatic lighting controls could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 585766.8495 | 314.5685 | 377482.2162 | 46861.348 | 8.0553 | 2.023% | 0
13 | halls | Lighting - controls | Localised lighting | 100% | 30% | Localised lighting could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 836809.785 | 449.3836 | 224691.7954 | 66944.7828 | 3.3564 | 2.89% | 0
14 | halls | Lighting - replacement fittings | Retrofit/replace lighting to T5 | 100% | 30% | Retrofit/replace lighting to T5 could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 133889.5656 | 71.9014 | 45513.5701 | 10711.1652 | 4.2492 | 0.4624% | 0
15 | halls | Misc | Awareness raising campaign | 100% | 30% | Awareness raising campaign could apply to 30% of our halls | Natural gas | 131552.1081 | Electricity (grid) | 234306.7398 | 150.1606 | 75080.2994 | 22691.1024 | 3.3088 | 0.9657% | 0
16 | halls | Misc | Equipment timer controls | 100% | 30% | Equipment timer controls could apply to 30% of our halls | Natural gas | 0 | Electricity (grid) | 78758.568 | 42.2949 | 12984.5423 | 6300.6854 | 2.0608 | 0.272% | 0
17 | Buildings Category 2 | BMS fine tuning | BMS fine tuning | 100% | 30% | BMS fine tuning could apply to 30% of our Buildings Category 2 | Natural gas | 90000 | Electricity (grid) | 22800 | 28.8914 | 13578.9373 | 4524 | 3.0015 | 0.1858% | 0
18 | Buildings Category 2 | Building fabric | Loft insulation | 100% | 30% | Loft insulation could apply to 30% of our Buildings Category 2 | Natural gas | 169090.9091 | Electricity (grid) | 0 | 31.2767 | 17702.6379 | 5072.7273 | 3.4898 | 0.2011% | 0
19 | Buildings Category 2 | Heating - controls | Heating control systems | 100% | 30% | Heating control systems could apply to 30% of our Buildings Category 2 | Natural gas | 507272.7273 | Electricity (grid) | 0 | 93.8302 | 60145.1815 | 15218.1818 | 3.9522 | 0.6034% | 0
20 | Buildings Category 2 | Heating - controls | Sequencing | 100% | 30% | Sequencing could apply to 30% of our Buildings Category 2 | Natural gas | 236727.2727 | Electricity (grid) | 0 | 43.7874 | 20580.0985 | 7101.8182 | 2.8979 | 0.2816% | 0
21 | Buildings Category 2 | Lighting - controls | Automatic lighting controls | 50% | 30% | Automatic lighting controls could apply to 15% of our Buildings Category 2 | Natural gas | 0 | Electricity (grid) | 199500 | 107.1355 | 128562.588 | 15960 | 8.0553 | 0.689% | 0
22 | Transport Category 1 | 0 | Effective travel plans | 50% | 100% | Effective travel plans could apply to 50% of our Transport Category 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 3
23 | Transport Category 1 | 0 | Low carbon replacement vehicles | 50% | 100% | Low carbon replacement vehicles could apply to 50% of our Transport Category 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0
24 | Transport Category 1 | 0 | Biodiesel replacement fuel | 50% | 100% | Biodiesel replacement fuel could apply to 50% of our Transport Category 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0
25 | Transport Category 1 | 0 | Fuel management | 50% | 100% | Fuel management could apply to 50% of our Transport Category 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0
26 | Transport Category 1 | 0 | Driver training & maintenance | 50% | 100% | Driver training & maintenance could apply to 50% of our Transport Category 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0
27 | business Air | 0 | Web Conference | 100% | 50% | Web Conference could apply to 50% of our business Air | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100

## Ease-effect
Ease and effect matrix |  |  | Bback to selection
EASE
EFFECT | 0 | 0 | 1
| 1 | 0 | 0
| 0 | 0 | 0
| Total opportunities | 2
1
7
4
5
2
3
6
9
8
The ease and effect matrix is a basic tool for swift assessment of projects. The idea is to quickly get from a long list of projects to three shorter lists, red/amber/green, with green projects the ones to follow up. This allows the carbon management team to focus on the opportunities that are most likely to provide the biggest savings for the least cost/effort. It is far from an accurate process, but is a useful step in the 'confidence curve' of quantification, shown below.
If a project is very easy (first column) and will have a high effect on emissions (top row), it will score 1.
If a project is difficult (last column) and will have a medium effect on emissions (bottom row), it will score 7.
The below table is generated automatically from ease-effect scores input on the "Opportunities" tab. For example if you put a project as "3" in the "Opportunities" tab, it will add one to the large number in the top right cell below.
Ease factors:
Cost (capital and revenue)
Cost (staff time)
Staff support
Technical practicality
Effect factors:
Carbon savings
Galvanising/engaging staff support
Public awareness

## Graphs&Analysis
Graphs and analysis
| Maximum potential if all projects were implemented | [5 empty] | Potential savings from selected projects
|  | Baseline emissions (tCO2/yr) | Remaining emissions (tCO2/yr) | Savings identified (tCO2/yr) | zero for wedges | % of total baseline |  | Baseline emissions (tCO2/yr) | Remaining emissions (tCO2/yr) | Savings identified (tCO2/yr) | zero for wedges | % of total baseline
| halls | 7150.5047 | 5519.9909 | 1630.5138 | 0 | 10.49% | halls | 7150.5047 | 5519.9909 | 1630.5138 | 0 | 10.49%
| Buildings Category 2 | 6300.992 | 5996.0707 | 304.9213 | 0 | 1.961% | Buildings Category 2 | 6300.992 | 5996.0707 | 304.9213 | 0 | 1.961%
| Buildings Category 3 | 2098.1898 | 2098.1898 | 0 | 0 | 0% | Buildings Category 3 | 2098.1898 | 2098.1898 | 0 | 0 | 0%
| Buildings Category 4 | 0 | 0 | 0 | 0 | 0% | Buildings Category 4 | 0 | 0 | 0 | 0 | 0%
| Buildings Category 5 | 0 | 0 | 0 | 0 | 0% | Buildings Category 5 | 0 | 0 | 0 | 0 | 0%
| Buildings Category 6 | 0 | 0 | 0 | 0 | 0% | Buildings Category 6 | 0 | 0 | 0 | 0 | 0%
| Buildings Category 7 | 0 | 0 | 0 | 0 | 0% | Buildings Category 7 | 0 | 0 | 0 | 0 | 0%
| Transport Category 1 | 0 | 0 | 0 | 0 | 0% | Transport Category 1 | 0 | 0 | 0 | 0 | 0%
| business Air | 0 | 0 | 0 | 0 | 0% | business Air | 0 | 0 | 0 | 0 | 0%
| Transport Category 3 | 0 | 0 | 0 | 0 | 0% | Transport Category 3 | 0 | 0 | 0 | 0 | 0%
| Transport Category 4 | 0 | 0 | 0 | 0 | 0% | Transport Category 4 | 0 | 0 | 0 | 0 | 0%
| Transport Category 5 | 0 | 0 | 0 | 0 | 0% | Transport Category 5 | 0 | 0 | 0 | 0 | 0%
| Transport Category 6 | 0 | 0 | 0 | 0 | 0% | Transport Category 6 | 0 | 0 | 0 | 0 | 0%
| Transport Category 7 | 0 | 0 | 0 | 0 | 0% | Transport Category 7 | 0 | 0 | 0 | 0 | 0%
| Renewables | N/A | N/A | 0 | 0 | 0% | Renewables | N/A | N/A | 0 | 0 | 0%
| Demand not considered | 0 | 0 | 0 | 0 | 0% | Demand not considered | 0 | 0 | 0 | 0 | 0%
| Totals | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45% | Totals | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45%
|  | Baseline emissions (tCO2/yr) | Remaining emissions (tCO2/yr) | Savings identified (tCO2/yr) | zero for wedges | % of total baseline |  | Baseline emissions (tCO2/yr) | Remaining emissions (tCO2/yr) | Savings identified (tCO2/yr) | zero for wedges | % of total baseline
| Buildings | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45% | Buildings | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45%
| Transport | 0 | 0 | 0 | 0 | 0% | Transport | 0 | 0 | 0 | 0 | 0%
| Renewables | N/A | N/A | 0 | 0 | 0% | Renewables | N/A | N/A | 0 | 0 | 0%
| Demand not considered | 0 | 0 | 0 | 0 | 0% | Demand not considered | 0 | 0 | 0 | 0 | 0%
| Totals | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45% | Totals | 15549.6865 | 13614.2515 | 1935.4351 | 0 | 12.45%

## Export to CMPR
Export to CMPR
Project Ref. Number | Opportunity/project | Project start year | Predicted year of first energy savings | ACTUAL year of first energy savings | Capital Costs (£) | £ Operating Cost in yr 1 | Lifetime of project from start year (years) | Emissions Source 1 | Amount saved emissions source 1 | Emissions Source 2 | Amount saved Emissions Source 2
1 | Heating control systems could apply to 30% of our halls |  |  |  | 31397.7199 |  | 10 | Natural gas | 264812.6851 | Electricity (grid) | 0
2 | Optimum start controls could apply to 30% of our halls |  |  |  | 12931.3542 |  | 10 | Natural gas | 176541.7901 | Electricity (grid) | 0
3 | Sequencing could apply to 30% of our halls |  |  |  | 10743.4736 |  | 10 | Natural gas | 123579.2531 | Electricity (grid) | 0
4 | Zoning could apply to 30% of our halls |  |  |  | 11135.3328 |  | 10 | Natural gas | 88270.895 | Electricity (grid) | 0
5 | Pipework insulation could apply to 30% of our halls |  |  |  | 5742.6337 |  | 10 | Natural gas | 65776.054 | Electricity (grid) | 0
6 | Fuel switching to biofuel could apply to 30% of our halls |  |  |  | 223309.1923 |  | 10 | Natural gas | 1503452.664 | Electricity (grid) | 0
7 | Upgrade to condensing boilers could apply to 30% of our halls |  |  |  | 55827.2981 |  | 10 | Natural gas | 375863.166 | Electricity (grid) | 0
8 | IT Management software could apply to 30% of our halls |  |  |  | 9326.0312 |  | 10 | Natural gas | 0 | Electricity (grid) | 59068.926
9 | LCD flat screens could apply to 30% of our halls |  |  |  | 133292.4599 |  | 10 | Natural gas | 0 | Electricity (grid) | 59068.926
10 | Printer rationalisation could apply to 30% of our halls |  |  |  | 38065.4336 |  | 10 | Natural gas | 0 | Electricity (grid) | 59068.926
11 | Virtualisation/thin computers could apply to 30% of our halls |  |  |  | 16019.2033 |  | 10 | Natural gas | 0 | Electricity (grid) | 49224.105
12 | Automatic lighting controls could apply to 30% of our halls |  |  |  | 377482.2162 |  | 10 | Natural gas | 0 | Electricity (grid) | 585766.8495
13 | Localised lighting could apply to 30% of our halls |  |  |  | 224691.7954 |  | 10 | Natural gas | 0 | Electricity (grid) | 836809.785
14 | Retrofit/replace lighting to T5 could apply to 30% of our halls |  |  |  | 45513.5701 |  | 10 | Natural gas | 0 | Electricity (grid) | 133889.5656
15 | Awareness raising campaign could apply to 30% of our halls |  |  |  | 75080.2994 |  | 10 | Natural gas | 131552.1081 | Electricity (grid) | 234306.7398
16 | Equipment timer controls could apply to 30% of our halls |  |  |  | 12984.5423 |  | 10 | Natural gas | 0 | Electricity (grid) | 78758.568
17 | BMS fine tuning could apply to 30% of our Buildings Category 2 |  |  |  | 13578.9373 |  | 10 | Natural gas | 90000 | Electricity (grid) | 22800
18 | Loft insulation could apply to 30% of our Buildings Category 2 |  |  |  | 17702.6379 |  | 10 | Natural gas | 169090.9091 | Electricity (grid) | 0
19 | Heating control systems could apply to 30% of our Buildings Category 2 |  |  |  | 60145.1815 |  | 10 | Natural gas | 507272.7273 | Electricity (grid) | 0
20 | Sequencing could apply to 30% of our Buildings Category 2 |  |  |  | 20580.0985 |  | 10 | Natural gas | 236727.2727 | Electricity (grid) | 0
21 | Automatic lighting controls could apply to 15% of our Buildings Category 2 |  |  |  | 128562.588 |  | 10 | Natural gas | 0 | Electricity (grid) | 199500
22 | Effective travel plans could apply to 50% of our Transport Category 1 |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
23 | Low carbon replacement vehicles could apply to 50% of our Transport Category 1 |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
24 | Biodiesel replacement fuel could apply to 50% of our Transport Category 1 |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
25 | Fuel management could apply to 50% of our Transport Category 1 |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
26 | Driver training & maintenance could apply to 50% of our Transport Category 1 |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
27 | Web Conference could apply to 50% of our business Air |  |  |  | 0 |  | 10 | 0 | 0 | 0 | 0
28 | [6 empty] | 10
29 | [6 empty] | 10
30 | [6 empty] | 10
31 | [6 empty] | 10
32 | [6 empty] | 10
33 | [6 empty] | 10
34 | [6 empty] | 10
35 | [6 empty] | 10
36 | [6 empty] | 10
37 | [6 empty] | 10
38 | [6 empty] | 10
39 | [6 empty] | 10
40 | [6 empty] | 10
41 | [6 empty] | 10
42 | [6 empty] | 10
43 | [6 empty] | 10
44 | [6 empty] | 10
45 | [6 empty] | 10
46 | [6 empty] | 10
47 | [6 empty] | 10
48 | [6 empty] | 10
49 | [6 empty] | 10
50 | [6 empty] | 10
51 | [6 empty] | 10
52 | [6 empty] | 10
53 | [6 empty] | 10
54 | [6 empty] | 10
55 | [6 empty] | 10
56 | [6 empty] | 10
57 | [6 empty] | 10
58 | [6 empty] | 10
59 | [6 empty] | 10
60 | [6 empty] | 10
61 | [6 empty] | 10
62 | [6 empty] | 10
63 | [6 empty] | 10
64 | [6 empty] | 10
65 | [6 empty] | 10
66 | [6 empty] | 10
67 | [6 empty] | 10
68 | [6 empty] | 10
69 | [6 empty] | 10
70 | [6 empty] | 10
71 | [6 empty] | 10
72 | [6 empty] | 10
73 | [6 empty] | 10
74 | [6 empty] | 10
75 | [6 empty] | 10
76 | [6 empty] | 10
77 | [6 empty] | 10
78 | [6 empty] | 10
79 | [6 empty] | 10
80 | [6 empty] | 10
81 | [6 empty] | 10
82 | [6 empty] | 10
83 | [6 empty] | 10
84 | [6 empty] | 10
85 | [6 empty] | 10
86 | [6 empty] | 10
87 | [6 empty] | 10
88 | [6 empty] | 10
89 | [6 empty] | 10
90 | [6 empty] | 10
91 | [6 empty] | 10
92 | [6 empty] | 10
93 | [6 empty] | 10
94 | [6 empty] | 10
95 | [6 empty] | 10
96 | [6 empty] | 10
97 | [6 empty] | 10
98 | [6 empty] | 10
99 | [6 empty] | 10
100 | [6 empty] | 10
Note on F5: If text changes to RED year is before project start date
Note on G5: To be completed once project is implemented
Note on J5: Please enter the number of years the project will last, e.g. new boiler lasts approximately 15 years. NPV calc works to a maximum of 25 years
Note on L5: A conversion assistant is available for energy statistics in other units. Follow hyperlink.
Note on N5: A conversion assistant is available for energy statistics in other units. Follow hyperlink.
The selected opportunities have been put into the Carbon Management Projects Register (CMPR) data input format.
The blue cells can be copied into the CMPR "Project list" tab. Use "paste special" and select "Values".

## References
References
|  | Benchmark electricity demand (kWh/m2/yr) | Benchmark fossil fuel demand (kWh/m2/yr) | Reference
| General Uni Campus Building | 80 | 24 | CIBSE TM46 and DEC benhcmark set
| Catering, bar/restaurant | 149 | 257 | CIBSE Guide F
| Catering, fast food | 218 | 618 | CIBSE Guide F
| Halls of residence | 100 | 290 | CIBSE Guide F
| Lecture room, arts | 76 | 120 | CIBSE Guide F
| Lecture room, science | 129 | 132 | CIBSE Guide F
| Library, air conditioned | 404 | 245 | CIBSE Guide F
| Library, naturally ventilated | 64 | 161 | CIBSE Guide F
| Residential self catering | 54 | 240 | CIBSE Guide F
| Science laboratory | 175 | 132 | CIBSE Guide F
| Office - AirCon Prestige type4 | 304.3 | 170.85 | ECG019
| Office - AirCon Standard type3 | 203.4 | 160.2 | ECG019
| Office - No AirCon Cellular type1 | 51.3 | 143.45 | ECG019
| Office - No AirCon OpenPlan type2 | 80.75 | 143.45 | ECG019
| Leisure Centre (Dry) | 105 | 343 | ECG087
| Leisure Centre (Lrg Pool) | 258 | 1321 | ECG087
| Leisure Centre (Sml Pool) | 237 | 1336 | ECG087
| Emissions Source | kgCO2/kWh | Reference
| Electricity (grid) | 0.53702 | Defra GHG emission factors, July 2008
| Natural gas | 0.18497 | Defra GHG emission factors, July 2009
| Petrol | 0.24119 | Calculated from below
| Diesel | 0.24356 | Calculated from below
| Aviation | 0.258 | Defra GHG emission factors, July 2008 (Aviation Turbine fuel)
kgCO2/litre
| Petrol use | 2.3154 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 6
| Diesel use | 2.6304 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 6
kgCO2/km
| Average petrol car | 0.207 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 6
| Average diesel car | 0.1979 | http://www.defra.gov.uk/environment/business/envrp/pdf/conversion-factors.pdf - Annex 6
l/km
| Average petrol car | 0.089401 | Derived from above
| Average diesel car | 0.075236 | Derived from above
kWh/litre
| Average petrol car | 9.6
| Average diesel car | 10.8
| Renewables |  |  | Reference
| Photovoltaics | 79 | kgCO2/m2 | ESD estimate using in house calculation tools
| Biomass | on buildings sheet
| Small wind (6kW turbines) | 3500 | kgCO2/turbine | ESD estimate using in house calculation tools
| Large wind (2MW turbines) | 2000000 | kgCO2/turbine | ESD estimate using in house calculation tools
| Solar hot water | 263 | kgCO2/system | ESD estimate using in house calculation tools
Current energy costs
| Electricity | 8 | p/kWh
| Gas | 3 | p/kWh
| Petrol | 90 | p/litre
| Diesel | 90 | p/litre
| Petrol | 9.375 | p/kwh
| Diesel | 8.3333 | p/kwh
| Aviation |  | p/kwh
| Petrol | 6.699 | p/km
| Diesel | 4.466 | p/km
| Petrol | 38.8702 | p/kgCO2
| Diesel | 34.2153 | p/kgCO2
| Aviation |  | p/kgCO2
% utility estimates are derived from CTV020 Further and Higher Education Sector Overview
Pick from list
YES
NO
Note on C63: Based on 38 mpg
Note on C64: based on 57mpg
Note on C65: Derived from above
Note on C66: Derived from above