## Guidance Notes
Voltage Management Load Mix Tool (Revision 1)
Guidance Notes
This tool is intended to give clients a standard format for recording their site load mix and voltage levels. The methodology used is derived from Carbon Trust guide CTG045. Salix asks that clients are familiar with the advice given in this guide before using this tool.
Click here to download Carbon Trust Guide CTG045 'Voltage management - An introduction to technology and techniques'
The table below is taken from CTG045 and gives guidance on which loads can be considered voltage dependent. We ask that clients ensure the data entered on the tool complies with this, as we will be unable to accept savings for loads classified by Carbon Trust as being voltage independent. We would also ask that particular attention is paid to those loads not classified as "Yes" or "No". These loads require additional consideration as to what extent they can be classed as voltage dependent, and for uncontrolled motors we require clients to complete our motor loading table.
| Load | Voltage Dependent
| Incandescent lamps | YES – Incandescent lamps (or bulbs) are a source of lighting where an electrical current runs through a filament that emits visible light. The most common types of incandescent lamps are standard tungsten filament, tungsten halogen and reflector lamps. All three of these are voltage dependent loads. Reducing the supply voltage to these lamps will result in a directly proportional reduction in power consumption. However, lower voltage and power will reduce the light output.
| Fluorescent lamps – inductive ballast (also known as switch start) | YES – An electrical ballast is required to strike (ignite) a fluorescent lamp. In older types an inductive (or magnetic) ballast is used. Simple magnetic ballasts provide an unregulated supply to the lamp with inductive and resistive impedance. In this arrangement the power consumed is proportional to the supplied voltage. However, lower voltage and power may reduce the light output. Rated light output is achieved within ±3% of 230V design voltage.
| Metal halide/SON lamps | POSSIBLY – These types of lamps have ballasts which can either be inductive or electronic. As per fluorescent lamps, depending upon the type of ballast, they can be either voltage dependent or voltage independent. The lighting supplier should be contacted to decide the type of ballasts you have and to determine their voltage dependency.
| Fluorescent lamps – electronic ballast (also known as high frequency) | NO – Modern fluorescent ballasts are electronically controlled to provide voltage at a higher than supplied frequency. This leads to improved efficiency in the production of light but also means they are voltage independent. Electronic ballasts are usually classified into those with either “passive” or “active” front ends. Those with passive front ends use discrete electronic components whilst those with active front ends use integrated circuits. In either case the process of conversion from mains frequency to a higher frequency result in the power demand being voltage independent.
| LED lamps | NO – LEDs have the same power demand, regardless of supply voltage, so energy consumed does not vary with voltage.
| Motor loads (Uncontrolled) | YES, IN MANY CASES – Most motors in use today are asynchronous induction motors. Large (>20kW) induction motors have low losses. When operating within 70-90 per cent of their rated output they are very efficient (as high as 95 per cent), and are effectively voltage independent. However, this is an ideal position. Most motors in use today are of a smaller rating and have higher losses making them less efficient. Many of these motors are oversized for their application and often operate for all or much of the time at partial load, which leads to increased losses. It is these losses which lead to a larger proportion of a motor’s power demand being voltage dependent. If motor loads form a significant part of your total site load, you should complete a detailed technical evaluation into the savings potential.
| Motor loads controlled by variable speed drive (VSD) | NO – no additional energy savings are possible through the reduction of supply voltage.
| Process loads | POSSIBLY – Process loads are generally electronically controlled to ensure that processes operate correctly. Most of the energy consumed in process plant will usually be by motors and heating. The potential for energy savings through voltage management is therefore dependent on how loads are controlled. You will need to seek specialist advice to assess the likely benefits of applying voltage management to process loads.
| Electric heating | PROBABLY NOT – Electric heating is a resistive load and as such a higher supply voltage will result in an increase in power demand. However like the electric kettle (page 6), the method of control is critical to whether energy consumption increases with higher voltages. Where temperature controllers, such as thermostats, are installed and are set correctly, energy consumption will not change with an increased supply voltage. Instead instantaneous power demand will be higher and heaters will warm up quicker.
| Electronic loads and information and computer technology (ICT) | NO – Most electronic (i.e. low power) equipment is designed for world markets. For example computer power supplies, mobile phone chargers and office equipment can accept a wide range of input voltages while operating with fixed DC voltages. The majority of electronic equipment relies on regulated power supplies, which consume the same energy over a wide range of input voltages. The potential energy savings through voltage management are therefore negligible.

## Site 1
Voltage Management Load Mix Tool (Revision 1)
© Salix Finance 2011
Site Name
|  | Pre-Project Annual Electricity Consumption (kWh) |  | Optimisation Setting (%)
|  | Current Site Voltage (V) |  | Site voltage after optimisation (V)
|  | Voltage Dependent Load | Percentage of Overall Load | Voltage Independent Load | Percentage of Overall Load
1
2
3
4
5
6
|  | TOTAL | 0% | TOTAL | 0%
|  |  | Total Load Check | 0%
Uncontrolled Motor, Chiller, Pump and Compressor Loads
The savings potential for uncontrolled motors in dependent on the extent to which the motors are oversized and/or are lightly used/loaded
Where voltage dependent savings are significantly dominated by uncontrolled motor loads, we would ask clients to complete the table below.
|  | Size of Motor (kW) | Number of Motors | Average Loading (%) | Percentage of Uncontrolled Motor Load (%)
|  |  |  | Total | 0%

## Site 2
Voltage Management Load Mix Tool (Revision 1)
© Salix Finance 2011
Site Name
|  | Pre-Project Annual Electricity Consumption (kWh) |  | Optimisation Setting (%)
|  | Current Site Voltage (V) |  | Site voltage after optimisation (V)
|  | Voltage Dependent Load | Percentage of Overall Load | Voltage Independent Load | Percentage of Overall Load
1
2
3
4
5
6
|  | TOTAL | 0% | TOTAL | 0%
|  |  | Total Load Check | 0%
Uncontrolled Motor, Chiller, Pump and Compressor Loads
The savings potential for uncontrolled motors in dependent on the extent to which the motors are oversized and/or are lightly used/loaded
Where voltage dependent savings are significantly dominated by uncontrolled motor loads, we would ask clients to complete the table below.
|  | Size of Motor (kW) | Number of Motors | Average Loading (%) | Percentage of Uncontrolled Motor Load (%)
|  |  |  | Total | 0%

## Site 3
Voltage Management Load Mix Tool (Revision 1)
© Salix Finance 2011
Site Name
|  | Pre-Project Annual Electricity Consumption (kWh) |  | Optimisation Setting (%)
|  | Current Site Voltage (V) |  | Site voltage after optimisation (V)
|  | Voltage Dependent Load | Percentage of Overall Load | Voltage Independent Load | Percentage of Overall Load
1
2
3
4
5
6
|  | TOTAL | 0% | TOTAL | 0%
|  |  | Total Load Check | 0%
Uncontrolled Motor, Chiller, Pump and Compressor Loads
The savings potential for uncontrolled motors in dependent on the extent to which the motors are oversized and/or are lightly used/loaded
Where voltage dependent savings are significantly dominated by uncontrolled motor loads, we would ask clients to complete the table below.
|  | Size of Motor (kW) | Number of Motors | Average Loading (%) | Percentage of Uncontrolled Motor Load (%)
|  |  |  | Total | 0%

## Site 4
Voltage Management Load Mix Tool (Revision 1)
© Salix Finance 2011
Site Name
|  | Pre-Project Annual Electricity Consumption (kWh) |  | Optimisation Setting (%)
|  | Current Site Voltage (V) |  | Site voltage after optimisation (V)
|  | Voltage Dependent Load | Percentage of Overall Load | Voltage Independent Load | Percentage of Overall Load
1
2
3
4
5
6
|  | TOTAL | 0% | TOTAL | 0%
|  |  | Total Load Check | 0%
Uncontrolled Motor, Chiller, Pump and Compressor Loads
The savings potential for uncontrolled motors in dependent on the extent to which the motors are oversized and/or are lightly used/loaded
Where voltage dependent savings are significantly dominated by uncontrolled motor loads, we would ask clients to complete the table below.
|  | Size of Motor (kW) | Number of Motors | Average Loading (%) | Percentage of Uncontrolled Motor Load (%)
|  |  |  | Total | 0%

## Site 5
Voltage Management Load Mix Tool (Revision 1)
© Salix Finance 2011
Site Name
|  | Pre-Project Annual Electricity Consumption (kWh) |  | Optimisation Setting (%)
|  | Current Site Voltage (V) |  | Site voltage after optimisation (V)
|  | Voltage Dependent Load | Percentage of Overall Load | Voltage Independent Load | Percentage of Overall Load
1
2
3
4
5
6
|  | TOTAL | 0% | TOTAL | 0%
|  |  | Total Load Check | 0%
Uncontrolled Motor, Chiller, Pump and Compressor Loads
The savings potential for uncontrolled motors in dependent on the extent to which the motors are oversized and/or are lightly used/loaded
Where voltage dependent savings are significantly dominated by uncontrolled motor loads, we would ask clients to complete the table below.
|  | Size of Motor (kW) | Number of Motors | Average Loading (%) | Percentage of Uncontrolled Motor Load (%)
|  |  |  | Total | 0%